## Quantities by area
Snowflake 7 Times Square fl. 29-31 - Perimeter linear diffusers (SD R2 clouds) - Northern Wolves AC - 10/05/2026
Floor | Area | Location | LD qty | CFM each | CFM total | 12x10 qty | 12x10 total in | 10x8 qty | 10x8 total in | VD/CO tagged | Main in bubbled area (ref.) | Notes | Material $ | Labor MH | Total $
29 | 29-1 | North-east corner, W 42nd St / Broadway | 4 | 300 / 300 / 300 / 300 | 1200 | 4 | 25 | 0 | 0 | 4 | 31.3/12 approx. 16 LF; 26.1/10 with offset down approx. 6 LF; 14"Ø approx. 6 LF | 2 diffusers along 42nd St off the 31.3/12 main, 2 along Broadway off the 26.1/10 / 14"Ø run.
29 | 29-2 | Seventh Ave, north | 3 | 265 / 270 / 265 | 800 | 3 | 33 | 0 | 0 | 3 | 29.3/10 approx. 13 LF
29 | 29-3 | Seventh Ave, Open Office 29.42 | 6 | 265 / 265 / 270 / 265 / 270 / 265 | 1600 | 6 | 66 | 0 | 0 | 2 | 26.1/10 approx. 20 LF (with tee) | VD/CO tagged on 2 of 6 connections.
29 | 29-4 | Broadway, north | 2 | 200 / 200 | 400 | 2 | 14 | 0 | 0 | 2 | 34.4/12 approx. 8 LF
29 | 29-5 | Seventh Ave, south (north end of sheet B) | 4 | 300 / 300 / 300 / 300 | 1200 | 4 | 40 | 0 | 0 | 4 | 31.3/12 approx. 12 LF; 14"Ø approx. 8 LF
29 | 29-6 | Seventh Ave, south | 4 | 300 / 300 / 300 / 300 | 1200 | 3 | 30 | 1 | 10 | 3 | 14"Ø approx. 13 LF; 29.3/10 approx. 7 LF | Last connection 10x8. VD/CO tagged on 3 of 4.
29 |  | 29th floor total
30 | 30-1 | Seventh Ave, north | 3 | 265 / 270 / 265 | 800 | 3 | 33 | 0 | 0 | 3 | 26.1/10 approx. 12 LF
30 | 30-2 | Seventh Ave, Open Office 30.35 | 5 | 300 / 300 / 300 / 200 / 200 | 1300 | 5 | 47 | 0 | 0 | 5 | 26.1/10 approx. 12 LF; 12"Ø approx. 9 LF | 3 off the 26.1/10, 2 off the 12"Ø below the 19x15.
30 | 30-3 | South wall (W 41st St side) | 4 | 300 / 300 / 300 / 300 | 1200 | 4 | 44 | 0 | 0 | 4 | 32.2/16 approx. 40 LF
30 |  | 30th floor total
31 | 31-1 | Seventh Ave, north (Focus Rm 31.65 / Corridor 31.51) | 2 | 200 / 200 | 400 | 2 | 18 | 0 | 0 | 1 | 26.1/10 approx. 4 LF (at elbow)
31 | 31-2 | Seventh Ave, Huddle Rms 31.46 / 31.47 | 3 | 265 / 270 / 265 | 800 | 3 | 36 | 0 | 0 | 0 | 28.1/12 approx. 15 LF | No VD/CO tags shown.
31 | 31-3 | Seventh Ave, at IDF 31.44 (match line) | 1 | 300 | 300 | 1 | 9 | 0 | 0 | 0 | 34.4/12 (same run as 31-4) | No VD/CO tag shown.
31 | 31-4 | Seventh Ave, 7P Meeting Rm 31.43 | 3 | 300 / 300 / 300 | 900 | 3 | 27 | 0 | 0 | 0 | 34.4/12 approx. 20 LF | No VD/CO tags shown.
31 | 31-5 | Seventh Ave, south | 3 | 265 / 270 / 265 | 800 | 3 | 27 | 0 | 0 | 0 | 28.1/12 approx. 15 LF | No VD/CO tags shown.
31 | 31-6 | Broadway, south | 2 | 300 / 300 | 600 | 2 | 14 | 0 | 0 | 2 | 29.3/10 approx. 13 LF
31 |  | 31st floor total
TOTAL