## Breakdown by area
COP-SF-05 Bulletin 3 Revision - Snowflake Fitout, 7 Times Square Fl 29-31 - Northern Wolves AC - 09/30/2026
Floor | Area | Description | Disconnect MH | Disconnect $ | Ductwork material $ | Install MH | Install labor $ | Air outlet material $ | Air outlet MH | Air outlet labor $ | Shop drawings $ | Total $
29 | 29-1 | North supply main - reroute through existing beam cuts | 12 |  | 6075 | 60 |  | 0 | 0 |  | 0
29 | 29-2 | Supply main resized 56x16 to 42x12 | 7 |  | 3900 | 50 |  | 0 | 0 |  | 0
29 | 29-3 | FPB-HW-E (1400) relocation and discharge reroute | 2 |  | 750 | 12 |  | 0 | 0 |  | 0
29 |  | Shop drawings for revised design | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000
29 |  | 29th floor total
30 | 30-1 | IT Build Rm 30.23 / F&B Storage 30.14 / west dining | 6 |  | 1700 | 30 |  | 500 | 0 |  | 0
30 | 30-2 | Lounge 30.02 - new transfer ducts | 0 |  | 2150 | 26 |  | 0 | 0 |  | 0
30 | 30-3 | Meeting Rms 30.04 / 30.05, Storage 30.09, Vestibule 30.07 | 16 |  | 0 | 24 |  | 0 | 0 |  | 0
30 |  | Shop drawings for revised design | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000
30 |  | 30th floor total
31 | 31-1 | Zoom rooms, northwest - transfer ducts | 1 |  | 330 | 6 |  | 0 | 0 |  | 0
31 | 31-2 | Transfer duct TD 32x16, north | 1 |  | 300 | 5 |  | 0 | 0 |  | 0
31 | 31-3 | Storage 31.02 - new transfer ducts | 0 |  | 1700 | 20 |  | 0 | 0 |  | 0
31 | 31-4 | Coffee Bar 31.12 - transfer ducts and main fitting | 6 |  | 1700 | 24 |  | 0 | 0 |  | 0
31 | 31-5 | Transfer duct TD 32x16, southwest | 4 |  | 650 | 16 |  | 0 | 0 |  | 0
31 | 31-6 | Storage 31.15 / Room 31.16, southeast | 5 |  | 900 | 12 |  | 0 | 0 |  | 0
31 |  | Shop drawings for revised design | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000
31 |  | 31st floor total
TOTAL COP-SF-05

## Area scope
Area | Floor | Title | Before (Addendum 1, installed) | After (Bulletin 3) | Work required
29-1 | 29 | North supply main - reroute through existing beam cuts | 46x16 supply main (approx. 20 LF, bottom el. 9'-9") with branch connections to FPB-HW-D (1500), FPB-HW-B (450) and FPB-B (200). | Main rerouted as 22x10 and 30x10 through (2) existing beam cuts, 30x10 aligned with the beam running plan northeast. New 14ø branch to FPB-HW-D, 10ø to FPB-HW-B and 6ø to FPB-B. | Disconnect and remove installed 46x16 section and branch connections. Fabricate and install 22x10 / 30x10 duct and round branches with insulation, reconnect terminal units.
29-2 | 29 | Supply main resized 56x16 to 42x12 | 56x16 supply main, approx. 44 LF, top el. 11'-1" / bottom el. 9'-9", Break Rm 29.57 to P.E. | Main resized to 42x12 on the same route, top el. 11'-1" / bottom el. 10'-1". | Disconnect and remove installed 56x16 main. Fabricate and install 42x12 main with insulation, reconnect branch takeoffs (FPB-HW-E, FPB-B (260)).
29-3 | 29 | FPB-HW-E (1400) relocation and discharge reroute | FPB-HW-E (1400) with inlet and 30x10 discharge to the G(400) / G(200) linear diffusers along the northeast wall. | FPB-HW-E relocated; inlet connection and 30x10 discharge elbow rerouted. | Disconnect inlet and discharge, relocate and rehang FPB-HW-E, fabricate and install new inlet and 30x10 discharge fittings, reconnect.
30-1 | 30 | IT Build Rm 30.23 / F&B Storage 30.14 / west dining | 12x10 branch with (2) C(220) ceiling diffusers; G(400) linear diffuser run on 16x12 branch. | 12x10 branch and (2) C(220) deleted, replaced with 10ø branch to (1) new G(440) linear diffuser. New 40x20 transfer duct at F&B Storage 30.14. G(400) linear diffusers relocated along the 16x12 branch. | Disconnect and remove 12x10 branch and (2) C(220). Install 10ø branch, 40x20 transfer duct, rework 16x12 branch. F&I G(440) linear diffuser with plenum, relocate G(400) diffusers.
30-2 | 30 | Lounge 30.02 - new transfer ducts | No transfer ducts at Lounge 30.02 walls. | (2) new 48x24 transfer ducts. | Fabricate and install (2) 48x24 lined transfer ducts.
30-3 | 30 | Meeting Rms 30.04 / 30.05, Storage 30.09, Vestibule 30.07 | FPB-HW-B (300) with supply connections; 44x20 transfer duct; (2) 12x12 grilles; 12ø branch to FPB-HW-D (1200). | 44x20 transfer duct relocated; (2) 12x12 grilles relocated to 5P / 7P Meeting; 12ø branch rerouted. | Disconnect and remove affected duct, fittings and grilles. Install 44x20 transfer duct and 12ø branch at new locations.
31-1 | 31 | Zoom rooms, northwest - transfer ducts | (1) transfer duct (not sized on Addendum 1). | TD 24x12 and new TD 18x12. | Remove existing transfer duct; fabricate and install TD 24x12 and TD 18x12.
31-2 | 31 | Transfer duct TD 32x16, north | Transfer duct as installed per Addendum 1 (not sized on Addendum 1). | Transfer duct revised to TD 32x16. | Remove installed transfer duct; fabricate and install TD 32x16.
31-3 | 31 | Storage 31.02 - new transfer ducts | No transfer ducts; volume damper at FPB-HW-B (500) branch. | (2) new 44x22 transfer ducts. | Fabricate and install (2) 44x22 lined transfer ducts.
31-4 | 31 | Coffee Bar 31.12 - transfer ducts and main fitting | 36x18 main with elbow at Coffee Bar 31.12; no transfer ducts. | (2) new TD 28x16; 36x18 main elbow reconfigured. | Disconnect and remove 36x18 elbow; fabricate and install new fitting and (2) TD 28x16.
31-5 | 31 | Transfer duct TD 32x16, southwest | Transfer duct and duct elbow as installed per Addendum 1, next to the 12x8 branch. | Transfer duct revised to TD 32x16; elbow deleted. | Remove installed transfer duct and elbow; fabricate and install TD 32x16.
31-6 | 31 | Storage 31.15 / Room 31.16, southeast | 12x12 and 18x12 grilles at previous locations; no transfer duct at Storage 31.15. | New TD 48x24; 12x12 and 18x12 grilles relocated. | Remove grilles and their duct connections; fabricate and install TD 48x24, relocate 12x12 and 18x12 grilles with duct connections at new locations.